## Compliance Report
File Name | Category | ID | Requirement | Rationale | Guidance | Status | Explanation | Evidence | Recommendations
1SDH002289A1002.pdf | SG | 1.a | Product defense in depth A process shall exist to create product user documentation that describes the security defense in depth strategy for the product to support installation, operation and maintenance that includes: a) security capabilities implemented by the product and their role in the defense in depth strategy. | This process is required to ensure that documentation for the defense in depth strategy is produced to support hardening of the product at the customer site. Such documentation is required by IEC 62443-2-4, that defines security requirements for IACS installation and maintenance service providers. Having this process means that the product supplier documents various aspects of the defense in depth strategy necessary to harden the product during installation and keep it hardened during its lifetime of use. Aspects of the defense in depth strategy to be documented include the residual threats that are expected to be present and capable of attacking the product, the security capabilities of the product to safeguard it against these threats and any compensating security controls/mitigations that can be used with the product to further protect the product. | End-user documentation (ie technical catalogue, manual…) shall include security capabilities of the product. | Partially Met | The manual describes some security capabilities such as HTTPS, user management with RBAC, TPM 2.0, port/service management, and NTP synchronization. However, it does not present these as part of a structured defense in depth strategy or explain their role within such a strategy. | • By default, the web server uses the HTTPS secure protocol. [page 7] • There are five user types: Administrator, Developer, Engineer, Operator and Guest. [page 17] • Cyber security: TPM 2.0 [page 16] • Allows you to upload the .pxf file containing the HTTPS certificate. [page 26] • Note: by default, a self-signed certificate is present. It is strongly recommended to replace this with a certificate issued by a trusted PKI. [page 26] • To protect Lite Panel Pro and ensure it works as intended, connect Lite Panel Pro to a reliable network, i.e. one that is strictly limited and controllable. [page 7] | Per the 3HKR000004 ELSP Cyber Security User Manual Template, add a dedicated section (e.g. '1.3. Defense in depth in Product') that explicitly lists all product security capabilities (secure protocols, user account management, certificate handling, secure boot, session timeout, audit logging, secure firmware updates, secure storage) and describes each capability's role in the overall defense in depth strategy.
1SDH002289A1002.pdf | SG | 1.b | Product defense in depth A process shall exist to create product user documentation that describes the security defense in depth strategy for the product to support installation, operation and maintenance that includes: b) threats addressed by the defense in depth strategy | This process is required to ensure that documentation for the defense in depth strategy is produced to support hardening of the product at the customer site. Such documentation is required by IEC 62443-2-4, that defines security requirements for IACS installation and maintenance service providers. Having this process means that the product supplier documents various aspects of the defense in depth strategy necessary to harden the product during installation and keep it hardened during its lifetime of use. Aspects of the defense in depth strategy to be documented include the residual threats that are expected to be present and capable of attacking the product, the security capabilities of the product to safeguard it against these threats and any compensating security controls/mitigations that can be used with the product to further protect the product. | End-user documentation (ie technical catalogue, manual…) or in deployment guidelines document shall include threats addressed by the defence in depth strategy. | Not Met | The manual does not identify or document specific threats addressed by the product's defense in depth strategy. There is no threat enumeration or threat model discussion. |  | Per the 3HKR000004 ELSP Cyber Security User Manual Template (section 1.3.1), add a section titled 'Threats addressed by product' that lists specific threats the product is designed to counter, such as: improper and invalid input, excessive network communication, unsolicited error & exception, communication tampering and spoofing, firmware tampering, and unauthorized modification of product configuration and parameters.
1SDH002289A1002.pdf | SG | 1.c | Product defense in depth A process shall exist to create product user documentation that describes the security defense in depth strategy for the product to support installation, operation and maintenance that includes: c) product user mitigation strategies for known security risks associated with the product, including risks associated with legacy code. | This process is required to ensure that documentation for the defense in depth strategy is produced to support hardening of the product at the customer site. Such documentation is required by IEC 62443-2-4, that defines security requirements for IACS installation and maintenance service providers. Having this process means that the product supplier documents various aspects of the defense in depth strategy necessary to harden the product during installation and keep it hardened during its lifetime of use. Aspects of the defense in depth strategy to be documented include the residual threats that are expected to be present and capable of attacking the product, the security capabilities of the product to safeguard it against these threats and any compensating security controls/mitigations that can be used with the product to further protect the product. | End-user documentation (ie technical catalogue, manual…) or deployment guidelines document shall include known security risks. Mitigations to these risks shall be included as well. If no known security risks are documented, then none were identified during threat modeling, attack surface reduction or security design reviews. | Partially Met | The manual mentions some risks (e.g., Modbus lacking encryption, HTTP sending data in plain text) and provides partial mitigations (use HTTPS, connect to a reliable network). However, it does not provide a comprehensive list of known security risks or structured mitigation strategies, nor does it address risks associated with legacy code. | • The Modbus protocol does not provide encryption, authentication or integrity checking of the transmitted data. [page 7] • If you decide to enable the HTTP protocol, it will send data in plain text and can therefore be subject to interception by unauthorised persons. [page 7] • To protect Lite Panel Pro and ensure it works as intended, connect Lite Panel Pro to a reliable network, i.e. one that is strictly limited and controllable. In addition, restrict access to Lite Panel Pro to personnel authorised to make changes to the configuration. [page 7] | Per the 3HKR000004 ELSP Cyber Security User Manual Template (section 1.4), add a dedicated section for 'Product user mitigation strategies' that lists all known security risks (including risks from legacy code or third-party components) alongside specific mitigation recommendations in a structured table format with columns for protocol, port, known risk, and recommended mitigation.
1SDH002289A1002.pdf | SG | 2 | Defense in depth measures expected in the environment A process shall be employed to create product user documentation that describes the security defense in depth measures expected to be provided by the external environment in which the product is to be used (see Clause 6). NOTE These measures can also come from 10.5. | This process is required to ensure that documentation for the defense in depth strategy is produced to support hardening of the product at the customer site. Such documentation is required by IEC 62443-2-4, that defines security requirements for IACS installation and maintenance service providers. Having this process means that the product supplier ocuments various aspects of the defense in depth strategy necessary to harden the product during installation and keep it hardened during its lifetime of use. | End-user documentation (manual, catalogue…) must describe environmental requirements that must be satisfied by the user | Partially Met | The manual mentions some environmental defense measures expected from the customer (firewalls, authentication, encryption, anti-virus, secure network, physical access control). However, these are scattered across a legal disclaimer and brief notes rather than presented as a structured set of environmental security requirements. | • It is the sole responsibility of the customer to provide and continuously ensure a secure connection between the product Lite Panel Pro and the network. [page 6] • The customer is responsible for establishing and maintaining all appropriate measures (e.g. installation of firewalls, application of authentication measures, data encryption, installation of anti-virus software, etc.). [page 6] • Only trained and authorised personnel may access the cabinet in which Lite Panel Pro is installed. [page 15] • To access the cabinet where Lite Panel Pro is installed, use a key or tool. [page 15] • The network used to connect Lite Panel Pro to the Internet (IT network) must be on a different subnet than the network used to connect the local devices (OT network). [page 41] | Per the 3HKR000004 ELSP Cyber Security User Manual Template (section 1.2), add a dedicated section on 'Cyber Security consideration for system (IACS)' with a reference architecture diagram and structured description of environmental defense in depth measures required including network segmentation, firewalls, VPN tunnels, user and rights management, and physical security measures.
1SDH002289A1002.pdf | SG | 3.a | Security hardening guidelines A process shall be employed to create product user documentation that includes guidelines for hardening the product when installing and maintaining the product. The guidelines shall include, but are not limited to, instructions, rationale and recommendations for the following: a) integration of the product, including third-party components, with its product security context (see Clause 6) | This process is required to ensure that instructions that describe how to harden the product and keep it hardened are documented. Such documentation is required by IEC 62443-2-4 that defines security requirements for IACS installation and maintenance service providers. Having this process means that the product supplier creates user documentation that provides directions for hardening the product during installation and for keeping it hardened during the lifetime of the product use. This requirement recognizes that the security policies and requirements for customer sites are often different, and as a result, instructions for securely integrating the product into the customer site, configuring it appropriately and maintaining its security are necessary. | End-user documentation (manual, catalogue…) must describe hardening guidelines, instructions and recommendations. that should be adhered to when installing the product or system | Partially Met | The manual provides some installation-related hardening guidance such as network separation, firewall configuration, and third-party device integration via templates. However, it does not present comprehensive hardening guidelines specifically addressing secure integration of the product and its third-party components within the product security context. | • The network used to connect Lite Panel Pro to the Internet (IT network) must be on a different subnet than the network used to connect the local devices (OT network). [page 41] • Any firewall configured on the IT network should allow communications FROM and TO the DNS server configured on port 53/UDP. [page 41] • Lite Panel Pro also supports third-party devices. [page 10] • WARNING: Lite Panel Pro and Modbus TCP devices must be connected to the same private network as the customer. [page 9] | Per the 3HKR000004 ELSP Cyber Security User Manual Template (section 1.5.1 and 1.5.2), add a dedicated 'Hardening during Installation' section that provides step-by-step instructions for securely integrating the product (including third-party components) with its security context, covering network architecture, firewall rules, and secure communication setup.
1SDH002289A1002.pdf | SG | 3.b | Security hardening guidelines A process shall be employed to create product user documentation that includes guidelines for hardening the product when installing and maintaining the product. The guidelines shall include, but are not limited to, instructions, rationale and recommendations for the following: b) integration of the product’s application programming interfaces/protocols with user applications; | This process is required to ensure that instructions that describe how to harden the product and keep it hardened are documented. Such documentation is required by IEC 62443-2-4 that defines security requirements for IACS installation and maintenance service providers. Having this process means that the product supplier creates user documentation that provides directions for hardening the product during installation and for keeping it hardened during the lifetime of the product use. This requirement recognizes that the security policies and requirements for customer sites are often different, and as a result, instructions for securely integrating the product into the customer site, configuring it appropriately and maintaining its security are necessary. | If the product contains an API or a set of classes or objects that developers can use, then instructions, rationale, and recommendations for integrating user applications securely with the API shall be provided in the end-user documentation. | Partially Met | The manual documents protocols (Modbus RTU/TCP) and the Protocol Translator feature for SCADA integration, and mentions the web server API. However, it does not provide security-specific hardening instructions or recommendations for securely integrating user applications with these interfaces/protocols. | • This feature allows external systems (e.g. SCADA) to communicate with RTU devices connected to Lite Panel Pro, using the Modbus TCP connection to the panel. [page 53] • The Modbus protocol does not provide encryption, authentication or integrity checking of the transmitted data. [page 7] • For these reasons, communication between Lite Panel Pro and the control system is not totally secure. [page 7] | Per the 3HKR000004 ELSP Cyber Security User Manual Template (section 1.5.3), add API/protocol hardening guidance including: secure authentication for API access, rate limiting, logging of API requests, and specific recommendations for securing Modbus TCP communication when integrating with SCADA or other user applications.
1SDH002289A1002.pdf | SG | 3.c | Security hardening guidelines A process shall be employed to create product user documentation that includes guidelines for hardening the product when installing and maintaining the product. The guidelines shall include, but are not limited to, instructions, rationale and recommendations for the following: c) applying and maintaining the product’s defense in depth strategy (see Clause 7); | This process is required to ensure that instructions that describe how to harden the product and keep it hardened are documented. Such documentation is required by IEC 62443-2-4 that defines security requirements for IACS installation and maintenance service providers. Having this process means that the product supplier creates user documentation that provides directions for hardening the product during installation and for keeping it hardened during the lifetime of the product use. This requirement recognizes that the security policies and requirements for customer sites are often different, and as a result, instructions for securely integrating the product into the customer site, configuring it appropriately and maintaining its security are necessary. | End-user documentation (manual, catalogue…) must describe the user responsibility for operating and maintaining the defence in depth strategy defined for the product or system | Not Met | The manual does not describe the user's responsibility for applying and maintaining the product's defense in depth strategy over time. There is no structured guidance on maintaining the defense in depth strategy post-installation. |  | Per the 3HKR000004 ELSP Cyber Security User Manual Template (section 1.5.3 'Hardening during Operation and Maintenance'), add a section describing the user's ongoing responsibilities for maintaining the defense in depth strategy, including: ensuring only authorized users have access, regularly checking firmware updates, reviewing and deleting unused accounts, maintaining backups, and reviewing audit logs.
1SDH002289A1002.pdf | SG | 3.d | Security hardening guidelines A process shall be employed to create product user documentation that includes guidelines for hardening the product when installing and maintaining the product. The guidelines shall include, but are not limited to, instructions, rationale and recommendations for the following: d) configuration and use of security options/capabilities in support of local security policies, and for each security option/capability: 1) its contribution to the product’s defense in depth strategy (see Clause 7); 2) descriptions of configurable and default values that include how each affects security along with any potential impact each has on work practices; and 3) setting/changing/deleting its value; | This process is required to ensure that instructions that describe how to harden the product and keep it hardened are documented. Such documentation is required by IEC 62443-2-4 that defines security requirements for IACS installation and maintenance service providers. Having this process means that the product supplier creates user documentation that provides directions for hardening the product during installation and for keeping it hardened during the lifetime of the product use. This requirement recognizes that the security policies and requirements for customer sites are often different, and as a result, instructions for securely integrating the product into the customer site, configuring it appropriately and maintaining its security are necessary. | End-user documentation (manual, catalogue…) must describe all security configuration options including default and recommended settings. | Partially Met | The manual documents some security options with their default values (e.g., port table with default open/closed status, HTTPS enabled by default, services enable/disable page, default passwords). However, it does not explain the contribution of each option to the defense in depth strategy, nor does it describe the security impact of changing each setting. | • By default, the web server uses the HTTPS secure protocol. [page 7] • Note: by default, a self-signed certificate is present. It is strongly recommended to replace this with a certificate issued by a trusted PKI. [page 26] • The administrator is advised to change all default passwords (see User management) after the first login. [page 17] • Note: logout occurs automatically after 3 hours of inactivity. [page 21] | Per the 3HKR000004 ELSP Cyber Security User Manual Template, add a comprehensive section listing all security configuration options (services, ports, passwords, certificates, session timeout) with: 1) their contribution to defense in depth, 2) default vs. recommended values and security impact of each, and 3) step-by-step instructions for setting/changing/deleting each value.
1SDH002289A1002.pdf | SG | 3.e | Security hardening guidelines A process shall be employed to create product user documentation that includes guidelines for hardening the product when installing and maintaining the product. The guidelines shall include, but are not limited to, instructions, rationale and recommendations for the following: e) instructions and recommendations for the use of all security-related tools and utilities that support administration, monitoring, incident handling and evaluation of the security of the product. | This process is required to ensure that instructions that describe how to harden the product and keep it hardened are documented. Such documentation is required by IEC 62443-2-4 that defines security requirements for IACS installation and maintenance service providers. Having this process means that the product supplier creates user documentation that provides directions for hardening the product during installation and for keeping it hardened during the lifetime of the product use. This requirement recognizes that the security policies and requirements for customer sites are often different, and as a result, instructions for securely integrating the product into the customer site, configuring it appropriately and maintaining its security are necessary. | If such tools exist their usage shall be described in the end-user documentation (manual, catalogue…). If the tools themselves are not secure, the end-user documentation shall indicate that these tools should be removed from the system prior to completing the integration. | Not Met | The manual does not provide instructions or recommendations for security-related tools and utilities that support administration, monitoring, incident handling, or evaluation of the product's security posture. |  | Per the 3HKR000004 ELSP Cyber Security User Manual Template, add a section documenting any security-related tools or utilities (e.g., log viewers, diagnostic tools, security monitoring capabilities) with usage instructions. If no such tools exist, explicitly state so. If tools are not secure, indicate they should be removed after integration.
1SDH002289A1002.pdf | SG | 3.f | Security hardening guidelines A process shall be employed to create product user documentation that includes guidelines for hardening the product when installing and maintaining the product. The guidelines shall include, but are not limited to, instructions, rationale and recommendations for the following: f) instructions and recommendations for periodic security maintenance activities. | This process is required to ensure that instructions that describe how to harden the product and keep it hardened are documented. Such documentation is required by IEC 62443-2-4 that defines security requirements for IACS installation and maintenance service providers. Having this process means that the product supplier creates user documentation that provides directions for hardening the product during installation and for keeping it hardened during the lifetime of the product use. This requirement recognizes that the security policies and requirements for customer sites are often different, and as a result, instructions for securely integrating the product into the customer site, configuring it appropriately and maintaining its security are necessary. | End-user documentation (manual, catalogue…) must include instructions and recommendations for periodic security maintenance activities to be done on the product. | Partially Met | The manual mentions software updates and provides a link for update instructions, and mentions battery replacement as periodic maintenance. However, it does not provide structured periodic security maintenance activities such as regular password rotation, certificate renewal, log review, or firmware update schedules. | • The guidelines for updating Lite Panel Prosoftware are available at the following link. [page 56] • Lite Panel Pro is updated to the latest version available. [page 43] | Per the 3HKR000004 ELSP Cyber Security User Manual Template (section 1.5.3), add a dedicated section on periodic security maintenance activities including: regular firmware update checks, periodic password changes, certificate renewal procedures, audit log review schedules, backup verification, and user account reviews.
1SDH002289A1002.pdf | SG | 3.g | Security hardening guidelines A process shall be employed to create product user documentation that includes guidelines for hardening the product when installing and maintaining the product. The guidelines shall include, but are not limited to, instructions, rationale and recommendations for the following: g) instructions for reporting security incidents for the product to the product supplier. | This process is required to ensure that instructions that describe how to harden the product and keep it hardened are documented. Such documentation is required by IEC 62443-2-4 that defines security requirements for IACS installation and maintenance service providers. Having this process means that the product supplier creates user documentation that provides directions for hardening the product during installation and for keeping it hardened during the lifetime of the product use. This requirement recognizes that the security policies and requirements for customer sites are often different, and as a result, instructions for securely integrating the product into the customer site, configuring it appropriately and maintaining its security are necessary. | End-user documentation (manual, catalogue…) must contain procedures for reporting security vulnerabilities back to the product manufacturer. | Not Met | The manual provides a general support email but does not include specific instructions or procedures for reporting security incidents or vulnerabilities to ABB. |  | Per the 3HKR000004 ELSP Cyber Security User Manual Template (section 1.6 'Vulnerability management'), add a dedicated section with the ABB Cyber Security Portal URL (https://www.abb.com/cybersecurity) and instructions for reporting security incidents and vulnerabilities, including a recommendation to sign up for security notification emails.
1SDH002289A1002.pdf | SG | 3.h | Security hardening guidelines A process shall be employed to create product user documentation that includes guidelines for hardening the product when installing and maintaining the product. The guidelines shall include, but are not limited to, instructions, rationale and recommendations for the following: h) description of the security best practices for maintenance and administration of the product. | This process is required to ensure that instructions that describe how to harden the product and keep it hardened are documented. Such documentation is required by IEC 62443-2-4 that defines security requirements for IACS installation and maintenance service providers. Having this process means that the product supplier creates user documentation that provides directions for hardening the product during installation and for keeping it hardened during the lifetime of the product use. This requirement recognizes that the security policies and requirements for customer sites are often different, and as a result, instructions for securely integrating the product into the customer site, configuring it appropriately and maintaining its security are necessary. | End-user documentation (manual, catalogue…) must describe how to administer the product in a secure manner (unless the product does not have administrative capability) | Partially Met | The manual describes some administrative best practices such as changing default passwords, using HTTPS, restricting access to authorized personnel, and using trusted PKI certificates. However, these are fragmented and not presented as a cohesive set of security best practices for maintenance and administration. | • The administrator is advised to change all default passwords (see User management) after the first login. [page 17] • In addition, restrict access to Lite Panel Pro to personnel authorised to make changes to the configuration. [page 7] • Note: by default, a self-signed certificate is present. It is strongly recommended to replace this with a certificate issued by a trusted PKI. [page 26] • Lite Panel Pro must be used by qualified personnel who have read all installation instructions. [page 6] | Per the 3HKR000004 ELSP Cyber Security User Manual Template (section 1.5.3), consolidate and expand security best practices for administration and maintenance into a dedicated section covering: principle of least privilege for accounts, ensuring only necessary services are running, regular log analysis, backup management, and physical access restrictions.
1SDH002289A1002.pdf | SG | 4 | Secure disposal guidelines A process shall be employed to create product user documentation that includes guidelines for removing the product from use. The guidelines shall include, but is not limited to, instructions and recommendations for the following: a) removing the product from its intended environment (see Clause 6); b) including recommendations for removing references and configuration data stored within the environment; c) secure removal of data stored in the product; and d) secure disposal of the product to prevent potential disclosure of data contained in the product that could not be removed as described in c) above. | This process is required to ensure that instructions that describe how to securely take the product out of use (decommission it) are documented. Such documentation is required by IEC 62443-2-4, that defines security requirements for IACS installation and maintenance service providers. Having this process means that the product supplier creates user documentation that provides directions for sanitizing the product of sensitive, confidential and/or proprietary data and software. | End-user documentation (manual, catalogue…) must include disposals about how to remove securely the product from use addressing the following issues: a) removing the product from its intended environment (note, depending on the product, this may not have any security implications) b) including recommendations for removing references and configuration data stored within the environment, (this may or may not apply) c) secure removal of data stored in the product, (this usually involves destroying or erasing hard disks) d) secure disposal of the product to prevent potential disclosure of data contained in the product that could not be removed as described in c) above | Partially Met | The manual has a Disposal section (7.5) addressing environmental disposal per EU WEEE directive, and mentions hard reset that erases all data. However, it does not provide security-specific disposal guidelines such as secure removal of sensitive data, configuration data cleanup, certificate/account deletion, or secure destruction of storage media. | • As prescribed by European Directive 2012/19/EU, do not dispose of this product together with unsorted municipal waste. [page 61] • Performs a full reset to the factory settings of the device. [page 57] • Data saved in Lite Panel Pro will be lost and will no longer be recoverable. [page 57] | Per the 3HKR000004 ELSP Cyber Security User Manual Template (section 1.5.4 'Hardening during Decommissioning'), add a dedicated secure disposal section covering: deleting user accounts, deleting certificates, deleting application and user data, removing product references from the environment, and secure destruction of storage media (referencing NIST 800-88 for embedded flash memory).
1SDH002289A1002.pdf | SG | 5 | Secure operation guidelines A process shall be employed to create product user documentation that describes: a) responsibilities and actions necessary for users, including administrators, to securely operate the product; and b) assumptions regarding the behaviour of the user/administrator and their relationship to the secure operation of the product. | This process is required to ensure that instructions that describe the secure use of the product during its operation and administration are included in the security guidelines. Having this process means that the product supplier creates user/administrator documentation that provides instructions for using the product securely. In general, this represents a set of best practices for the secure use of the product. For example, this could include guidelines for certificate management, password management and other authentication mechanisms. | End-user documentation (manual, catalogue…) must include assumptions regarding the behavior of the user/administrator. This means that it should describe the best practices or recommend behavior of users and administrators while operating the product. | Partially Met | The manual partially describes user responsibilities and roles (Administrator responsibilities for user management, qualified personnel requirement). However, it does not explicitly document assumptions regarding user/administrator behavior and their relationship to secure operation of the product. | • The administrator is the person responsible for Lite Panel Pro. The administrator is responsible for ensuring that all persons who connect to Lite Panel Pro are authorised to do so. [page 17] • Lite Panel Pro must be used by qualified personnel who have read all installation instructions. [page 6] • Remote control of any device should only be carried out by properly trained personnel [page 46] • Only trained and authorised personnel may access the cabinet in which Lite Panel Pro is installed. [page 15] | Per the 3HKR000004 ELSP Cyber Security User Manual Template, add a dedicated section on secure operation guidelines that explicitly states: a) all responsibilities and actions for users and administrators to operate the product securely, and b) assumptions about expected user/administrator behavior (e.g., users are trusted, trained, and follow password policies; administrators regularly review access controls).
1SDH002289A1002.pdf | SG | 6 | Account management guidelines A process shall be employed to create product user documentation that defines user account requirements and recommendations associated with the use of the product that includes, but is not limited to: a) user account permissions (access control) and privileges (user rights) needed to use the product, including, but not limited to operating system accounts, control system accounts and data base accounts; and b) default accounts used by the product (for example, service accounts) and instructions for changing default account names and passwords. | This process is required to ensure that requirements for the user accounts necessary to use the product are defined and documented. Having this process means that the product supplier creates documentation that defines accounts and their settings, including default accounts, that are needed to use the product. | End-user documentation (manual, catalogue…) must include account management guidelines. More specifically must include information about user account permissions and privileges required to use the product as well as default accounts used by the product and instructions for changing usernames and passwords on these accounts. ABB products shall not have any accounts (individual, shared, debug, etc.) that are not documented (note: does not necessarily require to disclose access credentials). | Partially Met | The manual documents five user types with a permissions matrix and provides default passwords. It also describes how to change/reset passwords. However, it does not describe operating system-level accounts, service accounts (e.g., SSH maintenance access), or provide instructions for changing default account names (only passwords). | • There are five user types: Administrator, Developer, Engineer, Operator and Guest. [page 17] • The administrator is advised to change all default passwords (see User management) after the first login. [page 17] • Administrator: Administrator#1 [page 17] • Developer: Developer#1 [page 17] • Engineer: Engineer#1 [page 17] • Operator: Operator# 1 [page 17] • Guest: Guest#1 [page 17] • Only the administrator has the permissions to enable or disable other users and can change the passwords of all users. [page 17] | Per the 3HKR000004 ELSP Cyber Security User Manual Template (section 1.3.2.4), document all accounts including OS-level and service accounts (e.g., SSH maintenance account), provide instructions for changing default account names where possible, and describe password complexity requirements. Add a table mapping all roles to their access rights following the RBAC concept.
1SDH002289A1002.pdf | SG | 7.a | Documentation review A process shall be employed to identify, characterize and track to closure errors and omissions in all user manuals including the security guidelines to include: a) coverage of the product’s security capabilities. | This process is required to ensure that the security-related documentation for the product is accurate and complete and that non-secure practices are not documented in other user documentation. Having this process means that the product's security-related documentation is reviewed to determine whether any product security capabilities have not been correctly or adequately addressed, and whether the documentation adequately describes how the product's defense in depth strategy is to be integrated with the product security context; and if discrepancies are found, that a process exists for addressing them. | Verify that there is evidence that the security guidelines were reviewed (such as meeting minutes or a review signoff). Verify that the review confirmed that all security capabilities are described in the security guidelines. This can be verified by a completed checklist, a comment in the meeting minutes or something similar. | Not Met | The manual contains no evidence of a documentation review process, review sign-off, or confirmation that all security capabilities have been reviewed for coverage in the security guidelines. |  | Implement a documentation review process per IEC 62443-4-1 SG-7. Maintain evidence such as review meeting minutes, completed checklists, or sign-off records confirming that all product security capabilities are accurately and completely described in the security guidelines.
1SDH002289A1002.pdf | SG | 7.b | Documentation review A process shall be employed to identify, characterize and track to closure errors and omissions in all user manuals including the security guidelines to include: b) integration of the product with its intended environment (see Clause 6). | This process is required to ensure that the security-related documentation for the product is accurate and complete and that non-secure practices are not documented in other user documentation. Having this process means that the product's security-related documentation is reviewed to determine whether any product security capabilities have not been correctly or adequately addressed, and whether the documentation adequately describes how the product's defense in depth strategy is to be integrated with the product security context; and if discrepancies are found, that a process exists for addressing them. | Verify that issues found during the user manual reviews are documented and tracked to closure. This can all be documented in the meeting minutes, through an issue tracking system, or thorough a similar method. | Not Met | The manual contains no evidence of a review process that addresses integration of the product with its intended environment, nor any issue tracking for documentation errors or omissions. |  | Implement a documentation review process that specifically verifies the manual adequately describes product integration with its intended environment. Track any identified issues to closure using an issue tracking system or documented meeting minutes.
1SDH002289A1002.pdf | SG | 7.c | Documentation review A process shall be employed to identify, characterize and track to closure errors and omissions in all user manuals including the security guidelines to include: c) assurance that all documented practices are secure. | This process is required to ensure that the security-related documentation for the product is accurate and complete and that non-secure practices are not documented in other user documentation. Having this process means that the product's security-related documentation is reviewed to determine whether any product security capabilities have not been correctly or adequately addressed, and whether the documentation adequately describes how the product's defense in depth strategy is to be integrated with the product security context; and if discrepancies are found, that a process exists for addressing them. | Verify that all user manuals were reviewed by security experts by reviewing meeting minutes and verifying that someone qualified as a security expert (Based on experience, education, or personal certification) was involved in reviewing each of the user manuals. | Not Met | The manual contains no evidence that documented practices have been reviewed by a security expert to assure all practices described are secure. |  | Ensure all user manuals are reviewed by a qualified security expert (based on experience, education, or certification). Document this review in meeting minutes with the security expert's name and qualifications, and verify that all documented practices are secure.
1SDH002289A1002.pdf | SG | ABB-SDLC-10 | Legal Disclaimer A process shall be employed to create product user documentation that includes ABB legal disclaimer regarding cyber security. |  | End-user documentation (ie technical catalogue, manual…) shall include legal disclaimers regarding cyber security as defined in 9ADB006607 | Fully Met | The manual includes a dedicated 'Cyber security legal disclaimer' section that clearly states customer responsibilities for network security, measures to be taken, and ABB's limitation of liability regarding security breaches. | • Lite Panel Pro is designed to be connected and to communicate information and data via a network interface, which should be connected to a secure network. It is the sole responsibility of the customer to provide and continuously ensure a secure connection between the product Lite Panel Pro and the network. [page 6] • The customer is responsible for establishing and maintaining all appropriate measures (e.g. installation of firewalls, application of authentication measures, data encryption, installation of anti-virus software, etc.). [page 6] • The user must protect the Lite Panel Pro product, the network, its systems and interface against any type of security breach, unauthorised access, interference, intrusion, loss and/or theft of data or information. [page 6] • ABB and its affiliates are not liable for damages and/or losses related to such security breaches, unauthorized accesses, interference, intrusion, loss and/or theft of data or information. [page 6]